## Location Inspection Template
Location/Area | Equipment/Component | Type | Notes for Condition | Pass | Fail | Recommendations/Corrective Actions | Photo | Follow Up Action
Exterior/Grounds/Structure | Roof System (Shingles, EPDM,Flat Roof, Flashing, Vents) |  | Age, remaining lifespan, missing/damaged/curling materials, water ponding, proper sealing, condition of skylights.
| Foundation/Slab/Grading |  | Visible cracks, signs of settling, water intrusion/dampness in basement/crawlspace, drainage away from structure.
| Siding/Walls |  | Cracks, holes, loose or rotting materials, peeling paint, proper caulking/sealing, signs of water penetration.
| Gutters & Downspouts |  | Clean, securely attached, proper slope and drainage, clear of debris, adequate run-off away from foundation.
| Walkways, Driveways, Parking Lots |  | Cracks, potholes, uneven surfaces, tripping hazards (1 inch or more height difference), visible parking striping/signage.
| Stairs, Decks, Porches, Balconies |  | Structural integrity, loose materials, wood rot, required and secure handrails/guardrails, proper height/spacing of railings.
| Security Features |  | Exterior lighting function, fencing/gates condition, functioning access control systems.
| Landscaping/Vegetation |  | Drainage is visible, Overgrowth, trees or shrubs touching the building or roof, vegetation near fire lanes, debris/rubbish accumulation.
| Parapet |  | Visual
| Windows |  | Visual
| Pool/Spa Area (If applicable) |  | Fencing and self-latching gates are in good working order, deck surface condition, clean and sanitary water.
Upper Roof | Elevators room, Water Tank, Cooling tower
Roof | Elevators room, MER, Boiler room
Exterior Stairs | Fire escape (if applicable) |  | Secure, Free of Rust and Debris
Interior stairs | Layout, Letters, Service |  | Emergency lighting, Cleanliness, Obstructions, Self closing doors
Common Areas | Hallways, Lobbies, Stairs |  | Clear of obstruction, functioning lighting, test emergency lighting, condition of flooring/carpeting, secure handrails.
| Laundry Facilities (Equipment & Room) |  | Ventilation (lint buildup), machine maintenance, floor drains clear, signs of water leaks/damage.
| Storage/Utility Rooms |  | Organization, fire separation/rated doors, presence of hazardous materials, clutter/combustibles.
| Common Area Fire Extinguishers |  | Present, properly mounted, current inspection tag (within 1 year), accessible, charged.
| Elevators (If applicable) |  | Up-to-date inspection certificate, overall operational condition, maintenance logs.
Mechanical | HVAC System(s) (Boilers, Furnaces, AC Units) |  | Age and condition, evidence of regular maintenance (clean filters/coils), proper venting, service records.
| Water Heaters/Boilers |  | Age, tank condition (rust/leaks), proper venting, functional pressure relief valve (PRV) and discharge pipe.
| Plumbing Systems (Visible Pipes, Fixtures) |  | Leaks, corrosion, signs of old/deteriorated pipe material (e.g., cast iron, polybutylene), proper drainage.
| Electrical Panel(s)/Wiring |  | Panel age/type (e.g., Zinsco, Federal Pacific are high-risk), circuit labeling, exposed/unsafe wiring, sufficient capacity, proper grounding.
| Fire Suppression/Sprinkler System (See Fire pump room template) |  | System inspection/service records, proper pressure, visible damage, adequate coverage.
Unit Interior | Smoke & Carbon Monoxide Detectors |  | Proper placement (bedrooms/halls), hardwired with battery backup, functionality (testing).
| Windows & Exterior Doors |  | Proper sealing/weather stripping, broken glass, secure locks, easy/proper function (e.g., emergency egress).
| Walls, Ceilings, Floors |  | Cracks, bubbling/stains on walls/ceilings (indicates water damage/leaks), condition of flooring, signs of mold/mildew.
| Bathroom/Kitchen Plumbing |  | Faucet/toilet leaks, under-sink leaks, evidence of water damage/mold behind fixtures.
Attic/Crawlspace | Insulation/Ventilation |  | Adequate and properly installed insulation, proper ventilation to prevent moisture/heat buildup.
| Structural Components (Rafters, Joists) |  | Evidence of moisture/water intrusion, signs of wood-destroying insects (termites, etc.).
Basement | Domestic booster room - See DBP tab
Fire pump - See FP Tab
| Storm dentention tank |  | Vented- Overflow protection
Telecom Room/ONT Service
Ejector Pits See Ejector Pit Template

## Domestic Water Tank Template
Location/Component | Equipment/Component | Key Inspection/Condition Notes (NYC Health Code & Insurance Risk Focus) | Pass | Fail | Photo | Follow up
I. NYC REGULATORY & DOCUMENTATION
Annual Inspection | DOH Report Filing | Inspection must be done at least once per calendar year by a Qualified Inspector (LMP, PE, or Architect). Results must be filed with the DOH by January 15 of the following year.
Cleaning/Disinfection | Permit & Records | Tank must be cleaned and disinfected at least annually (per Plumbing Code). Work must be done by a permitted vendor. Records must be kept on file for 5 years.
Water Quality | Bacteriological Sample | Annual water sample (post-cleaning/disinfection) to verify compliance with NYS Sanitary Code (Coliform test).
Public Notice | Resident Notification | Owner must post a notice in an accessible area stating that inspection results are available to residents upon request.
II. TANK STRUCTURE & EXTERIOR INTEGRITY
Material | Cedar etc.
Steel bands | Tight?
Tank Shell/Staves | Condition (Wood/Steel) | Visual check for cracking, warping, or separation of wood staves/hoops; excessive rust, corrosion, or pitting on steel tanks.
Roof | Tank Top/Lid | Must be watertight and intact; properly secured to prevent unauthorized access or contamination from windblown debris.
Access Hatch | Security & Screen | Must be locked/secured; openings (including vents) must be properly screened to prevent entry by birds, rodents, or insects.
Support Structure | Platform/Beams | Structural integrity of the entire support structure (especially critical for insurance); check for corrosion, cracks, or loose fasteners.
III. PIPING & OVERFLOW PREVENTION
Overflow Line | Function & Termination | Must be piped to a point that prevents damage to the building and is visible (to identify pump/float failure). Must be unobstructed.
Emergency Drain | Function | Accessible and ready for use; piping should allow the tank to be drained quickly for emergency maintenance.
High-Water Alarm | Required Safety | MUST be present and functional to alert building staff/control system to prevent tank overflow (NYC requirement).
Suction & Discharge | Piping | Inspect pipe runs leading to and from the tank for leaks, excessive rust, or deterioration of insulation.
IV. SANITARY & INTERNAL CONDITIONS (DOH Focus)
Internal Surface | Sediment/Growth | Look for presence of sediment, sludge, biofilm, algae, or biological growth (primary DOH concern for Legionella risk).
Foreign Matter | Debris/Contamination | No floatable debris, paint chips, or signs of insect/rodent activity inside or immediately adjacent to the tank.
Circulation | Inlet/Outlet Placement | Ensure piping design promotes adequate water circulation (i.e., prevents stagnant zones).

## Ejector Pit Template
Location/Component | Equipment/Component | Key Inspection/Condition Notes (Insurance Risk Focus) | Pass | Fail | Photo | Follow Up
PIT/BASIN & ENVIRONMENT
Pit/Basin | Cover/Sealing/Venting | Cover must be sealed tightly to prevent odor/gas/evaporation into the building. Pit size must be appropriate for pump.
| Pit Condition (Visual) | Excessive sediment, grease, or debris visible in the pit (causes clogs/float failure).
| Venting | Vent pipe must be clear and unobstructed to prevent vacuum lock or pressure buildup.
| High-Level Alarm | Alarm light/horn must be present and functioning (tested by lifting float); panel must be clearly labeled.
PUMP & MECHANICAL
Pump Unit | Visual Condition | Corrosion, rust, or scale buildup on the pump casing/motor; pump must be level and properly seated.
Quantity | Impeller (Inferred) | Observe pump flow: signs of a clogged impeller (slow drainage, excessive noise, or pump running but not moving water).
| Seals/Gaskets | Signs of leakage around the pump housing or discharge line connections.
| Noise/Vibration | Listen during operation: Unusual noises (grinding, rattling, clanging) indicate bearing failure or loose impeller/parts.
Float Switches | Functionality & Position | Test the switch (manually activate): must move freely without sticking/tangling in debris or wiring.
| Pump Cycling (Observed) | Check for short cycling (pump turning on/off too frequently) or constant running (indicates faulty float or clogged discharge).
PIPING & DISCHARGE
Discharge Line | Piping & Connections | Inspect visible pipe runs for leaks, cracks, or damage; ensure pipe diameter is sufficient.
| Check Valve | Must be present and functional on the discharge line to prevent wastewater from flowing back into the pit (causing short cycling).
| Gate/Isolation Valve | Present and accessible to allow pump isolation for maintenance.
ELECTRICAL & SAFETY
Power Supply | Wiring/Cord | Power cord must be in good condition (no splices or frays) and plugged into a dedicated outlet.
| Circuit Protection | Pump circuit must be connected to a GFCI (Ground-Fault Circuit Interrupter) outlet (critical safety measure, though nuisance tripping is a risk).
| Alarm Power | High-level alarm system should ideally have a separate or backup power source (e.g., battery).

## Cooling Tower Template
Location/Component | Inspection Item/Task | NYS Mandate & Insurance Risk Focus | Pass | Fail | Photo | Follow Up
I. NYS/NYC REGULATORY & DOCUMENTATION
Registration | NYS Cooling Tower Registry | Registration Number must be current; information updated at intervals not exceeding 90 days while in use.
Maintenance Program | Maintenance Program & Plan (MPP) | MPP must be kept on site (or adjacent building) for immediate inspection; must be updated annually or after system changes.
Certification | Annual Certification | Certification Date is recorded annually by Novemer1 by a Qualified Person (PE, CIH, CWT, or Consultant).
Records | Logbook/Retention | Records of all tests, inspections, and disinfections must be retained for a minimum of 3 years.
II. PHYSICAL TOWER CONDITION & DEFICIENCIES
Inspection Frequency | Compliance Inspection | Must be performed at intervals not exceeding 90 days while the tower is in use (by Qualified Person).
Tower Structure | Casing, Basin, Fill, Drift Eliminators | Check for corrosion, excessive scale, and visible damage/deterioration. Eliminators must be intact (to prevent water drift).
Contaminants | Basin and Interior Surfaces | Must be free of organic material, biofilm, sludge, algae, and debris (high Legionella risk factors).
Drift Eliminators | Condition and Integrity | Check for holes or gaps; must be fully intact to minimize aerosol generation into occupied areas.
Cleaning | Cleaning & Disinfection | Required at least twice annually (prior to seasonal start-up/shutdown) or whenever required by sample results.
III. WATER QUALITY MONITORING & TESTING
Water Treatment | Chemical Treatment Program | Verification that approved biocides and corrosion inhibitors are added daily while the tower is operational.
Bacteriological Indicator | Dip Slides | Sampling required at intervals not exceeding 30 days while in use (Responsible Person).
Pathogen Testing | Legionella Culture Analysis | Sampling required at intervals not exceeding 90 days while in use (by Qualified Person) and tested by NYS ELAP Certified Lab.
Reporting Results | Exceedance Notification | Documentation that the Local Health Department was notified within 24 hours if Legionella result is 1,000 CFU/mL or greater.
IV. MECHANICAL & OPERATIONAL CHECKS
Water Level Control | Make-up Water/Float Valve | Functional, ensuring continuous supply; check for leaks or signs of overflow.
Water Flow | Nozzles/Distribution System | Inspect for clogging or excessive scale/biofilm that disrupts water flow (creates dry spots, increasing risk).
Bleed/Blowdown | System Function | Functional to control Total Dissolved Solids (TDS) and conductivity (prevents scale/corrosion).
Mechanical Equipment | Fan, Motor, Belts, Pumps | Check for excessive vibration/noise; proper belt tension; functional safety guards in place.
Electrical | Wiring/Disconnects | Secure, clean connections; accessible and clearly marked emergency shut-off switch.

## Fire Pump Room Template
Location/Component | Equipment/Component | Key Inspection/Condition Notes (Insurance Risk & NFPA 25 Focus) | Pass | Fail | Photo | Follow up Action
I. FIRE PUMP ROOM & WATER SUPPLY
Pump Room/House | Temperature/Condition | Minimum 40∘F (70∘F for diesel with no engine heater). Room must be clean, dry, and free of storage/combustibles.
| Ventilation/Drainage | Ventilation louvers must be free to operate. Floor drains must be clear and functional.
| Foundation/Mounting | Pump and motor securely mounted; no visible cracks or signs of movement or excessive vibration.
Water Supply | Suction/Supply Tank (if applicable) | Tank must be full (check visually or through indicator); intake/screens are unobstructed.
| Valves | Suction, Discharge, and Bypass valves must be fully open and locked/supervised (tagged).
II. FIRE PUMP ASSEMBLY (Main Pump)
Visual/Physical Check | Pump Casing/Piping | No leaks (especially piping/fittings); casing free of excessive rust/corrosion.
| Shaft Seal/Packing Gland | Check during operation: Must show slight discharge (typically 10–60 drops per minute) to cool packing.
| Gauges | Suction and Discharge pressure gauges are functional, readable, and last calibrated date is current.
| Coupling | Coupling guard must be in place and secure; check for proper alignment.
III. PUMP DRIVER & POWER
Electric Motor | Controller/Selector | Controller pilot light (power on) must be illuminated. Selector switch must be set to "AUTO".
| Weekly Test | Run pump for 10 minutes (monthly for most electric pumps, weekly for non-pressurized supply).
| Transfer Switch (if on emergency power) | Check normal power light
Diesel Engine (If applicable) | Fuel System | Fuel tank must be at least 2/3 full
| Batteries | Two separate sets required; charger operational, proper voltage/amperage, clean/tight terminals.Distlilled water available.
| Engine Performance | Check oil level, coolant temperature/level, and oil pressure; run for 30 minutes weekly (no-flow/churn test).
IV. JOCKEY PUMP & PRESSURE CONTROL
Jockey Pump | Operation | Operational and automatically maintains correct system pressure.
| Settings | Cut-in and Cut-out settings are correct and do not overlap with the main fire pump's activation pressure.
| Maintenance | No visible leaks at seals; motor running smoothly.
V. TEST & ALARMS
Test Connections | Flow Test Header | Header valves are closed and ready for annual flow test; ensure adequate drainage outside.
Relief Valve | Circulation Relief Valve | Operational; discharges water when the pump runs at churn (no flow).
Alarms | Controller/Monitoring | Alarm pilots are off (no fault condition); test that all alarms signal correctly to the monitoring station.
Documentation | Logbook/Records | Weekly test data recorded (suction/discharge pressure, run time, oil/fuel levels); Annual flow test report on file.

## Heating Template
System Type/Location | Equipment/Component | Model | Serial | Key Inspection/Condition Notes (Insurance Risk Focus) | Pass | Fail | Photo | Follow Up Action
I. STEAM SYSTEMS (Boiler is the heat source)
Boiler Unit (Vessel) | ASME Nameplate and Jurisdictional Cert |  |  | Visible, legible; check stamped Max Allowable Working Pressure (MAWP); verify current inspection tag/certificate.
| Safety/Relief Valve |  |  | Correctly sized, current re-certification tag, non-threaded discharge pipe to within 6 inches of the floor.
| Low Water Cut-Off (LWCO) |  |  | Must be clean, operational (burner shuts down when tested/blown down), and piped correctly; check for sludge/sediment buildup.
| Water Level Gauge Glass |  |  | Clean, clear, visible, showing proper water level, fittings clear of obstructions.
| Hartford Loop (Varies by design) |  |  | Properly piped to protect boiler from running dry in case of a leak in the return line.
Distribution | Steam Traps (Return lines/Radiators) |  |  | Functional (not passing live steam or backing up condensate), signs of leaks.
| Condensate Receiver Tank & Pump |  |  | Tank free of rust/corrosion/leaks; pump operational and properly wired.
| Vacuum Pump (for 2-pipe systems) |  |  | Functioning to aid steam circulation and ensure condensate return; no leaks/excessive noise.
II. HYDRONIC SYSTEMS (Hot Water Boiler is the heat source)
Boiler Unit (Vessel) | Safety Relief Valve (T&P) |  |  | Rated 30 PSI maximum for low-pressure heat; check for leaks and proper discharge piping.
| Pressure/Altitude Gauge |  |  | Reading correct static pressure (cold) and operating pressure (hot); functioning.
| High Temperature Limit Control (Aquastat) |  |  | Functional and correctly set (typically manual reset on the high limit); check for signs of overheating.
| Expansion Tank |  |  | Correctly sized (often check if tank is "waterlogged" by tapping), check for leaks.
Distribution | Circulator Pumps |  |  | Functioning properly, no excessive noise/vibration/leaks, check for lubrication needs.
| Piping (Supply & Return) |  |  | Signs of leaks or heavy corrosion; condition of pipe insulation.
| Heat Emitters (Baseboard/Radiators/Fan Coils) |  |  | Free of leaks, adequate heat output, radiators secure.
III. FORCED AIR SYSTEMS (Furnace or RTU is the heat source)
Furnace/Air Handler | Heat Exchanger |  |  | Visual check for cracks or rust/corrosion (a critical CO risk); check flue draft.
| Burner/Ignition System |  |  | Clean, proper flame ignition and color; check safety controls (flame sensor).
| Air Filter |  |  | Clean and correctly sized; filter access door/panel secure.
| Blower Motor/Fan |  |  | Operational, proper speed/airflow, no excessive noise/vibration.
Distribution | Ductwork |  |  | Condition, signs of damage/crush/disconnection, insulation condition, presence in unconditioned spaces.
| Flue/Vent |  |  | Proper venting material and termination, secure connections, clear of obstructions.
| Carbon Monoxide (CO) Detector |  |  | Present and functioning near the equipment and in living spaces (critical life safety).
IV. HEAT PUMPS/ELECTRIC SYSTEMS (Decentralized or Central)
Air-Source Heat Pump (Split Systems, PTACs, Mini-Splits) | Outdoor Condensing Unit |  |  | Clean coil, level setting, clear of debris/snow/ice, sound level, condition of refrigerant lines (insulation).
| Indoor Air Handler/Fan Coil |  |  | Clean coil, proper condensate drainage (no leaks/overflowing pan), blower operation.
| Refrigerant Lines/Connections |  |  | Check for oil stains/ice (indicating a potential leak).
Electric Heat | Electric Baseboard Heaters |  |  | Securely mounted, clear of nearby combustibles (drapes, furniture), wiring secure.
Central VRF/Chiller Loop | VRF Main Controller/Outdoor Units |  |  | Operational, check for error codes, access to maintenance records.
General Safety | Emergency Shut-Off Switch |  |  | Clearly marked, accessible, and operational.

## HVAC Template
System Type/Location | Equipment/Component | Model | Serial | Key Inspection/Condition Notes (Insurance Risk Focus) | Pass | Fail | Photo | Follow Up Action
CENTRALIZED BOILER SYSTEMS (Steam & Hydronic)
Boiler Unit (Vessel) | Safety/Relief Valve (PRV/T&P) |  |  | Correct rating, current certification tag (if required by jurisdiction), proper discharge piping.
| Low Water Cut-Off (LWCO) / High Limit |  |  | Tested operational function (must shut off burner); check for sludge/corrosion.
| Expansion Tank |  |  | Correctly sized, no leaks, checked for waterlogging (hydronic only).
| Flue/Vent |  |  | Proper material, secure connections, no signs of rust/corrosion/back-drafting (CO risk).
Distribution | Circulator Pumps (Hydronic) |  |  | No leaks, proper alignment/lubrication, no excessive noise/vibration.
| Steam Traps / Condensate Pump |  |  | Functioning correctly (steam traps not leaking steam), condensate pump operational and no pan overflow/leakage.
COOLING TOWERS & CHILLER SYSTEMS (Central Cooling)
Cooling Tower | Structure/Casing/Fill |  |  | Structural integrity (no corrosion/wood decay), secure mounting on roof, condition of fill/drift eliminators.
| Basin & Water Quality |  |  | No excessive sludge/debris in basin (Legionella risk), functioning make-up water float valve (to prevent overflow).
| Mechanical Components |  |  | Fan/motor/gearbox/belts condition; check for excessive vibration (failure risk), operational vibration cut-out switch.
Chiller | Compressor/Vessel |  |  | No signs of oil/refrigerant leaks; check pressure/temp gauges; maintenance records.
| Water Loops |  |  | Proper flow, water treatment logs, no leaks/corrosion on chilled water pipes/insulation.
REFRIGERANT-BASED SYSTEMS (VRF, Split Systems, Heat Pumps)
Outdoor Unit (VRF/Condenser) | Mounting/Clearance |  |  | Secure mounting (on roof curbs or pad), adequate clearance for airflow.
| Refrigerant Piping/Valves |  |  | Visual inspection of accessible piping/Y-joints/headers; check insulation condition; no oil stains/frost (signs of leaks).
| Safety/Controls |  |  | Check for system fault codes on display; verify proper electrical disconnect.
Indoor Units (Fan Coils/Cassettes) | Refrigerant Charge / Leakage |  |  | For VRF/Mini-Splits: Room volume evaluation may be required for high refrigerant charge (safety/code risk).
| Condensate Drainage |  |  | Condensate pan and drain line clear and free of blockages/overflow (major interior water damage risk).
FORCED AIR SYSTEMS (Furnaces, RTUs, AHUs)
Heating/Combustion Section | Heat Exchanger (Furnaces/RTUs) |  |  | Critical check for rust/cracks/holes (primary source of CO poisoning risk).
| Flue/Vent |  |  | Proper material and termination, secure draft, no blockage.
Air Handling/Distribution | Filter/Coils |  |  | Clean coils, clean and correctly sized filter, no excessive moisture/biological growth.
| Ductwork |  |  | Visible leaks at seams/connections; condition of insulation (especially in attics).
| Blower/Motors |  |  | Functional, proper operation/airflow, belt condition (if applicable).
DECENTRALIZED/UNITARY SYSTEMS (PTAC/Electrical)
PTAC/PTHP Units (Through-Wall) | Sealing/Sleeve |  |  | Proper sealing of unit to exterior wall (water intrusion/energy loss risk), clean outdoor intake/filter.
Electric Baseboard/Heaters | Mounting/Clearance |  |  | Securely fastened, clearance from all combustible materials (drapes, furniture) at base and top.
ELECTRICAL & GENERAL SAFETY (Applies to All)
Electrical Supply | Disconnects/Wiring |  |  | Clearly marked, accessible, and functional emergency shut-off; check for loose/exposed wiring, correct fuse/breaker sizing.
Maintenance & Records | Logbooks/Tags |  |  | Evidence of recent professional service/tune-up (within the last 12 months for major systems); up-to-date inspection tags.
Life Safety | CO Detectors |  |  | Present and functioning where combustion equipment is located or where a refrigerant leak could concentrate.

## Domestic Booster Pumps Template
Location/Component | Equipment/Component | Key Inspection/Condition Notes (Insurance Risk Focus) | Pass | Fail | Photo | Follow Up Action
Pump Room/Environment | General Condition | Clean, dry, well-lit, no excessive water accumulation on the floor (leak indicator).
| Floor Drains | Clear and functioning to manage any system leaks or runoff.
| Temperature/Ventilation | Ambient temperature maintained (to prevent freezing or overheating of motors/VFDs).
Pump Assembly | Pumps (P1, P2, P3, etc.) | Visual leaks at pump seals, gaskets, or flanges (water damage risk).
| Motor Condition | No signs of overheating (discoloration, odor), check for unusual noise or excessive vibration during operation.
| Shaft/Couplings | Coupling guard securely in place; visible alignment check (misalignment causes bearing/seal failure).
| Mounting/Base | Securely anchored to the concrete pad/base; no signs of foundation cracking or movement.
Control System | Control Panel/VFD | Clean internal components, no signs of water intrusion or corrosion; all indicator lights are normal/green.
| Selector Switch | Check position (must be set to "AUTO" for automatic operation/alternation).
| Redundancy | Verify pump alternation sequence is functioning (to ensure even wear and standby capability).
| Low Suction Pressure Cutoff | Functional device set to shut down the system if supply water fails (protects pumps from dry running/overheating).
Pressure & Sensing | Pressure Gauges (Suction & Discharge) | Functional and readable, reflecting expected pressures; ensure pressure lines are not clogged/obstructed.
| Pressure Transducers (VFD Sensor) | Clean and functional (VFD systems rely on accurate pressure readings).
| Performance Check | Observe pressure stability under a simulated high-demand scenario.
Piping & Accessories | Hydro-Pneumatic/Bladder Tank | Tank integrity (no external rust/damage); air-side pressure check (requires maintenance).
| Check Valves | Inspect for proper operation and signs of "water hammer" (which damages components).
| Isolation Valves (Inlet/Outlet) | Fully open in normal operation; accessible and functional for service isolation.
| Backflow Prevention Device | Present, properly installed, and current inspection tag (required by code/utility).
Electrical System | Electrical Connections | Tightness of all terminal connections (loose connections cause arcing/fire); proper grounding.
| Circuit Protection | Correct breaker/fuse sizing; proper Lockout/Tagout (LOTO) procedures in place near the disconnect.
Documentation | Maintenance Log | Records of seal replacements, bearing lubrication, and annual system performance tests.
| Manufacturer Manuals | Accessible (digital or hardcopy) for operational reference.

## Swimming Pool Room Template
Location/Component | Equipment/Component | Key Inspection/Condition Notes (NYC Health/Safety/Energy Focus) | Pass | Fail | Photo | Follow Up
I. POOL AREA & SAFETY
Pool Vessel/Structure | Walls & Deck | Watertight and easily cleaned surfaces; check for cracks, sharp edges, or trip hazards on the deck (deck must slope away from the pool).
| Depth Markings | Permanent markings showing depth at shallow/deep ends and break points must be visible from both inside and outside the pool.
Perimeter/Deck | Walkway | Must have a walkway at least 5 feet wide around the entire perimeter (NYS Sanitary Code). Surface must be non-slip.
| Hand-Holds/Gutter | Continuous hand-hold provided by the coping or overflow gutter system. Gutter must be level and functional.
Life Safety | Ladders/Steps | Ladders or steps with handrails at the deep and shallow ends; treads must be non-slip.
| Drains/Suction | Entrapment protection for suction outlets is MANDATORY (dual drains, anti-entrapment covers, or SVRS/safety vacuum release system).
Barriers (Outdoor Only) | Fencing/Gates | Minimum 48 inches high barrier; gates must be self-closing and self-latching (latch at least 40 inches high).
II. POOL MECHANICAL ROOM (Plumbing & Filtration)
Environment | General Condition | Room must be clean, dry, and well-lit; floor drain is clear. Chemicals must be stored separately from mechanical/electrical equipment.
Recirculation Pumps | Operation & Leaks | Proper operation; check for leaks at seals and flanges; no excessive noise/vibration. Strainer basket must be clean.
Filters | Vessel Condition | Filter tanks must be free of corrosion; check gauge for correct operating pressure and backwash pressure.
Chemical Feed Systems | Chemical Storage | Chemicals must be stored and handled safely (e.g., chlorine and acid must be stored separately). Feed pumps must be functional.
| Disinfection | MANDATORY primary disinfection system (usually chlorine/bromine); check for functional automatic feed system.
Heating | Pool Heater | Heater is venting properly (if gas); no leaks in heat exchanger/plumbing. Check T&P valve (if applicable).
III. INDOOR POOL DEHUMIDIFICATION UNIT
Unit Condition | Casing & Sealing | Exterior casing intact and sealed; check for corrosion/rust due to high chlorine vapor content.
| Coils & Pans | Evaporator and Condenser coils must be clean; condensate drain pan must be clean and drain line must be clear (prevents overflow/mold).
Air Distribution | Ductwork/Diffusers | Ducts must be properly sealed and insulated; diffusers designed to provide air movement over the entire pool surface without causing drafts.
| Outdoor Air (Ventilation) | Unit must be configured to introduce the minimum required volume of outdoor air for ventilation (per ASHRAE 62.1/NYS Energy Code).
Controls | Humidity Setpoint | Unit must be maintaining space RH between 50%−60% (ideal range) and maintaining air temperature 2−4∘F above water temperature (prevents evaporation).
Energy Recovery | Heat Recovery | For pools over 500 ft2, the dehumidifier must include an energy recovery system capable of using the heat generated to heat the pool water (NYS Energy Code).

## Elevator Motor Room Template
Location/Component | Equipment/Component | Key Inspection/Condition Notes (NYC DOB & Safety Focus) | Pass | Fail | Photo | Follow Up Action
I. ROOM ACCESS & ENVIRONMENT
Access Door | Locking & Labeling | Door must be kept locked (key access restricted to authorized personnel). Door must be properly labeled ("ELEVATOR MACHINE ROOM" or similar).
Egress | Clear Path | Path of travel to exit must be kept clear and unobstructed; must swing out where possible.
Room Condition | Housekeeping & Storage | Room must be clean, dry, and free of storage of any tools, equipment, or materials not essential to the elevator (major fire/tripping risk).
Lighting | Illumination | Adequate, permanent lighting must be provided; emergency lighting must be functional.
Fire Suppression | Smoke Detection/Sprinklers | Must comply with code (e.g., typically no sprinklers are permitted in machine rooms unless specifically required by code and designed for water protection). Proper smoke detection must be present.
Ventilation | Air Conditioning/Venting | Independent ventilation or A/C system must be provided and operational to protect electrical equipment from overheating (NYC Building Code §3005.2).
II. MECHANICAL & ELECTRICAL
Controller/Drive | Condition | Clean, secure casing; no visible signs of arcing, overheating, or corrosion. Check for proper working clearances around the panel.
| Brake System | Check the brake assembly for function and wear. Traction elevators with single-plunger brakes must be upgraded to dual plunger or equivalent by January 1, 2027 (Local Law 126 of 2021).
Disconnect | Main Switch | Clearly marked, accessible, and lockable; switch must be sized correctly for the motor load.
Hydraulic Units (If applicable) | Tank & Piping | Tank oil level is correct; no visible leaks around tank, pumps, or piping; proper seismic bracing.
Governors | Governor Ropes/Sheaves | Check rope wear, proper tension, and sheave condition. Ensure governor is properly tagged and sealed.
Traction Machine | Sheaves/Ropes/Cables | Check rope wear and tension; check for oil leaks from bearings or gearbox (if geared).
III. DOCUMENTATION & COMPLIANCE (NYC DOB FILING)
Caertificates | For each elevator | Current
Current Contract | Maintenance Control Program (MCP) | Current MCP document must be maintained on file and readily accessible in the building.
Identification | Device ID Tag | Elevator must have a clear Device ID Tag and Alpha-numeric Bank Identification (NYC Fire Code).
Category 1 (CAT 1) Test | Annual Safety Test (No Load) | MUST be performed annually (between Jan 1 - Dec 31). Report must be filed with the DOB via DOB NOW: Safety within 21 days of the test date.
| Affirmation of Correction (AOC) | Defects found must be corrected within 90 days of the test date, and the AOC filed within 14 days of correction.
Category 5 (CAT 5) Test | Five-Year Full Load Test | MUST be performed every 5 years (verifying safety systems with 125% rated load). DOB must be notified 5 days prior to testing.
| Report Filing | Report must be filed with the DOB within 21 days of the test date. Failure to file on time results in significant penalties ($5,000 maximum).
Periodic Inspection | Visual Inspection | An additional annual visual inspection must be performed by an independent agency. Report filed within 14 days of inspection.
Maintenance Log | Record Keeping | A logbook/log must be kept in the machine room detailing all service visits, repairs, and part replacements.
Inspection Type | Frequency | Action | Deadline | Penalty Risk
Periodic Inspection | Annually | Visual inspection report filing by the inspection agency. | Within 14 days of the inspection date. | DOB violation/penalty for failure to file.
Category 1 (CAT 1) | Annually (Jan 1 – Dec 31) | Report of annual safety test (no load) filing by the inspection agency. | Within 21 days of the test date. | Penalty for late filing.
AOC (Affirmation of Correction) | After CAT 1 Test | Filing by owner/agent stating all defects found during CAT 1 are corrected. | Within 14 days of the correction date. (Corrections must be made within 90 days of test). | $1,000 for failure to file AOC.
Category 5 (CAT 5) | Every 5 years | Full load safety test report filing by the inspection agency. | Within 21 days of the test date. | Significant penalty, up to $5,000 for failure to file on time.